## Slide 1: Impedance analysis of harmonic resonance in HVDC connected Wind Power Plants
Master Thesis Project
Igor Sowa
July 2016

## Slide 2: Outline
Introduction
Motivation
Simulations description
Simulations results
Summary

## Slide 3: Introduction
Second RES
Wind power: 3.7% at the of 2015 global electricity production
In 2015 largest annual increase ever: 63.7 GW (~43% of all RES) – growth rate of 17.2% comparing to 2014
Record low prices for forthcoming RES in some countries due to policies and market frameworks
Figure 1: Wind Power Global Capacity and Annual Additions, 2005-2015.
Wind power capacity development

## Slide 4
Total of 12 GW
3.4 GW installed in 2015
3019 MW in Europe (more than twice than capacity added in 2014)
Trends in technology:
  Power of turbines
  Water depth
  Distance from shore (average of 43.3 km in 2015 only)
Introduction
Offshore WPP

## Slide 5
High capacitance of submarine cables
Charging current:
Limited active power transmission for ↑
Possible compensation
Introduction
Power transmission to shore

## Slide 6: Introduction
No charging current – no compensation
Lower transmission losses
Cheaper cable
Higher losses and risk of failure of converter
Should be decided on the project per project basis
HVDC transmission

## Slide 7: Motivation
Recent experience in operation of first HVDC connected offshore WPP (committed in 2013)
Phenomenon of harmonic resonance due to:
  AC network with many cables bringing down the resonant frequencies
  Power converter dominated grid with limited damping (weak grid, decoupled from main AC grid)
Necessity of harmonic resonance analysis for future project

## Slide 8: Simulations description
Test system topology cases

## Slide 9: Simulations description
Importance of converter modelling
Difficulty in detail data obtainment
Model as either ideal voltage or ideal current source
  Ideal VS becomes short-circuit in f domain
  Ideal CS becomes open-circuit in f domain
Converter models I

## Slide 10: Simulations description
Nonlinear impedance models:
  derived for WT inverter and HVDC-link rectifier
  harmonic linearization method
  positive- and negative-sequences
  valid below and above fundamental frequency
Converter models II

## Slide 11: Simulations description
WT inverter
HVDC-link rectifier
Converter models III

## Slide 12: Simulations description
Characterization of the system equivalent impedance at a bus in the system as a function of frequency
Frequency Sweep

## Slide 13: Simulations description
Based on admittance matrix Y and its eigenvalue analysis:
  In presence of very large element of inverted Y matrix, the Y matrix itself tends to singularity
  Y becomes singluar when even one of the eigenvalue becomes zero
  From eigenvalues: identification of critical modes of harmonic resonance
  Curves of modal impedance for each mode in modal domain
  Modes related to physical buses through participation factors (PF) defined as:
Harmonic Resonance Modal Analysis

## Slide 14: Simulations description
Only for Z(s) converter model
Model of aggregated impedance for source and grid
System is stable if satisfies Nyquist stability criterion
Division point
Souce-grid or grid-source apprach
Thevenin/Norton equivalent circuits
Stability analysis model

## Slide 15: Simulations description
Nyquist stability criterion in the Bode diagram
  Bode instead of Nyquist because of frequency information directly included
  Evaluation of stability for zero-dB crossings (intersection of source and grid impedances)
    At each intersection the phase angle is evaluated
  Due to assumptions safety margin of 30⁰ introduced
  Quality of stability evaluated by following phase margin at each resonant frequency:
Stability assessment

## Slide 16: Simulations description
Case 1
Case 2
Case 3
Impedance model

## Slide 17
WT inverter (100 MW)
HVDC rectifier (400 MW)
Simulations results
Nonlinear impedances of WT inverter and HVDC-link rectifier

## Slide 18
Simulations results
Case 2: Frequency sweep

## Slide 19
Simulations results
Case 2: Harmonic Resonance Modal Analysis – max. modes and all modes

## Slide 20
Simulations results
Case 2: Harmonic Resonance Modal Analysis – critical modes

## Slide 21
Chart: Case 2: VS model
8.46 | 5.3 | 7.9 | 8 | 8.7 | 9 | 9.2 | 12.5 | 8.7 | 9 | 9.2 | 12.5
12.12 | 0 | 0 | 0 | 0.2 | 0.3 | 1.1 | 48.4 | 0.2 | 0.3 | 1.1 | 48.4
12.23 | 0.3 | 0 | 0 | 0 | 0.1 | 0.8 | 48.9 | 0 | 0.1 | 0.8 | 48.9
23 | 0.6 | 8.9 | 9.6 | 13.6 | 14.2 | 11.7 | 1 | 13.6 | 14.2 | 11.7 | 1
Chart: Case 2: CS-WT model
7.77 | 1.7 | 3.2 | 3.2 | 4.2 | 4.6 | 5.8 | 31.3 | 4.2 | 4.6 | 5.8 | 31.3
9.51 | 0 | 0 | 0 | 0.1 | 0.3 | 1.1 | 48.5 | 0.1 | 0.3 | 1.1 | 48.5
10.25 | 1.5 | 1.1 | 1.1 | 0.4 | 0.2 | 0 | 47.4 | 0.4 | 0.2 | 0 | 47.4
22.98 | 0.6 | 8.9 | 9.6 | 13.7 | 14.3 | 11.8 | 0.7 | 13.7 | 14.3 | 11.8 | 0.7
Chart: Case 2: Z(s) model
9.51 | 1.8 | 3.5 | 3.6 | 4.6 | 5.1 | 6.1 | 29.7 | 4.6 | 5.1 | 6.1 | 29.7
12.34 | 0 | 0 | 0 | 0.2 | 0.3 | 1.1 | 48.4 | 0.2 | 0.3 | 1.1 | 48.4
23.11 | 0.7 | 8.8 | 9.5 | 13.6 | 14.2 | 11.7 | 1 | 13.6 | 14.2 | 11.7 | 1
Simulations results
Case 2: Harmonic Resonance Modal Analysis – participation factors

## Slide 22
Simulations results
Case 2: Verification in Power Factory

## Slide 23
Simulations results
Comparison between topology cases: FS – VS model
VS model
CS-WT model
Z(s) model

## Slide 24
Simulations results
Comparison between topology cases: HRMA – VS model

## Slide 25
Chart: 
8.59 | 8.8 | 12.8 | 13 | 14.2 | 14.6 | 15.1 | 21.5
12.17 | 0.1 | 0 | 0 | 0.2 | 0.4 | 1.8 | 97.4
23.7 | 0.9 | 14.6 | 15.7 | 23.1 | 24.3 | 20 | 1.4
Chart: 
8.46 | 5.3 | 7.9 | 8 | 8.7 | 9 | 9.2 | 12.5 | 8.7 | 9 | 9.2 | 12.5
12.12 | 0 | 0 | 0 | 0.2 | 0.3 | 1.1 | 48.4 | 0.2 | 0.3 | 1.1 | 48.4
12.23 | 0.3 | 0 | 0 | 0 | 0.1 | 0.8 | 48.9 | 0 | 0.1 | 0.8 | 48.9
23 | 0.6 | 8.9 | 9.6 | 13.6 | 14.2 | 11.7 | 1 | 13.6 | 14.2 | 11.7 | 1
Chart: 
7.55 | 2.5 | 4.8 | 4.9 | 5.1 | 5.2 | 5.2 | 5.2 | 5.1 | 5.2 | 5.2 | 5.2 | 4.9 | 5.1 | 5.2 | 5.2 | 5.2 | 5.1 | 5.2 | 5.2 | 5.2
12.1 | 0 | 0 | 0 | 0.1 | 0.2 | 0.6 | 24.2 | 0.1 | 0.2 | 0.6 | 24.2 | 0 | 0.1 | 0.2 | 0.6 | 24.2 | 0.1 | 0.2 | 0.6 | 24.2
12.12 | 0 | 0 | 0 | 0.2 | 0.3 | 1 | 46.6 | 0.2 | 0.3 | 1 | 46.6 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 1.8
12.3 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0.3 | 24.5 | 0 | 0 | 0.3 | 24.5 | 0.1 | 0 | 0 | 0.3 | 24.5 | 0 | 0 | 0.3 | 24.5
18.73 | 1.7 | 5.6 | 5.8 | 6.7 | 6.7 | 5.2 | 1.7 | 6.7 | 6.7 | 5.2 | 1.7 | 5.8 | 6.7 | 6.7 | 5.2 | 1.7 | 6.7 | 6.7 | 5.2 | 1.7
Simulations results
Comparison between topology cases: HRMA PF’s – VS model

## Slide 26
Simulations results
Comparison between topology cases: HRMA dominant buses – VS model

## Slide 27
Simulations results
Case 2: Stability I

## Slide 28
Simulations results
Case 2: Stability I

## Slide 29
marginally stable
unstable
Simulations results
FS vs. HRMA vs. Bode for all topology cases

## Slide 30
FS: parallel & series resonance frequencies seen from particular point in the network
HRMA: parallel resonant frequencies & participation factors indicating source bus(es) of resonance
Nyquist/Bode: parallel resonant frequencies & phase margin indicating quality of stability
Summary
Output from the methods

## Slide 31
More resonant frequncies for cases with multiple branches
Downward shift of resonance for topology cases with more cables (more capacitance):
New resonant frequencies have expected values and expected source due to symmetry in the network
All three models consistent with respect to sources of resonance
The resonance sourced near WT inverter is the ”stiffest”: minor shifting, highest PF’s and highest stability phase margin
Resonant frequencies of highest group (around 23th order) marked as unstable (unstable operation in case of presence of waveforms around this order)
Progressively worse stability phase margin for the topologies with more branches
Summary
Observations from simulations

## Slide 32
Recognition of resonant frequencies and their values and number in a network
Identification of origins of resonances indicating the best locations for filters implementation
Prediction of new resonances and their approximate origins after topology change
Labeling the resonances with respect to hazard for stability
Mitigation of resonance by adjusting of converter impedance (detailed control data necessary)
Summary
Conclusions

## Slide 33
Thank you!