## Slide 1: Impedance analysis of harmonic resonance in HVDC connected Wind Power Plants
Igor Sowa
19 July 2016
Master Thesis Project

## Slide 2: Content
Introduction
Motivation
Model description
    Converter models and other elements
    Methods
    Topology cases
Simulations results
Summary

## Slide 3: Introduction
Figure 1: Wind Power Global Capacity and Annual Additions, 2005-2015. [1]
Wind power capacity development
+63.7 GW (3.7%)
2015:
17.2% growth
The most incentives
Notes: - Second RES, after hydro
- Wind power: 3.7% at the of 2015 global electricity production
- In 2015 largest annual increase ever: 63.7 GW (~43% of all RES) – growth rate of 17.2% comparing to 2014
- Record low prices for forthcoming RES in some countries due to policies and market frameworks

## Slide 4: Introduction
12 GW total power
3.4 GW installed in 2015
3019 MW in Europe
Increase doubled comparing to 2014
Trends in technology:
  Power of turbines
  Water depth →
  Distance from shore →
Offshore WPP
Figure 2: Average water depth and distance to shore of online, under construction and consented wind farms. [2]
43.3 km in 2015 only

## Slide 5: Introduction
High capacitance of submarine cables
Charging current:
Limited active power transmission for ↑
Compensation possible
Power transmission to shore
Figure 3: Maximal transmitted power by AC cables with and without additional compensation. [3]

## Slide 6: Introduction
No charging current – no compensation
Lower transmission losses
Cheaper and simpler cable
Higher controllability
Higher losses and risk of failure of converter
Should be decided on the project per project basis
HVDC transmission
Figure 4: Energy transmission cost for HVAC and HVDC technologies. [4]
55-85 km

## Slide 7: Motivation
Recent experience in operation of first HVDC connected offshore WPP
Phenomenon of harmonic resonance due to:
    AC network with many cables bringing down the resonant frequencies
    Limited damping due to power converter dominated grid decoupled from main AC grid (weak grid)
Necessity of harmonic resonance analysis for future project

## Slide 8: Model description
    Converter models
    Methods
    Topology cases
    Modelling of other elements

## Slide 9: Model description
Importance of converter modelling
Difficulty in detail data obtainment
Converter models (I)
Figure 5: Voltage Source and Current Source models.
Model as either ideal voltage or ideal current source
  Ideal VS becomes short-circuit in f domain
  Ideal CS becomes open-circuit in f domain

## Slide 10: Model description
Nonlinear impedance models:
  derived for WT inverter and HVDC-link rectifier
  harmonic linearization method overcoming control nonlinearities
  positive and negative sequences of impedance
  valid below and above fundamental frequency
Converter models (II)
Figure 6: Control diagram of WT converter. [5]
Figure 7: Control diagram of HVDC converter. [5]

## Slide 11: Model description
WT inverter [6]
HVDC-link rectifier [6]
Converter models (III)
Figure 8: Diagram of WT converter in the considered study case.
Figure 9: Diagram of HVDC converter in the considered study case.

## Slide 12: Model description
Modelling of other elements
Transformers – inductance L
Filter reactors – inductance L
Filter shunt capacitances – capacitance C with resistance R
Cables – π (pi) model:
Figure 15: PI model of cable.

## Slide 13: Model description
Characterization of the system equivalent impedance at a bus in the system as a function of frequency
Methods (I): Frequency Sweep
Figure 11: Series resonance example.
Figure 10: Parallel resonance example.

## Slide 14: Model description
Method based on analysis of admittance matrix Y and its eigenvalues:
  In presence of a very large element of inverted Y matrix, the Y matrix itself tends to singularity
  Y becomes singular when even one of the eigenvalue becomes zero
  From eigenvalues we are able to identify critical modes of harmonic resonance
  As the result:
    curves of modal impedance for each mode in modal domain
    participation factors (PF) describing possible source of resonances, defined as:
Methods (II): Harmonic Resonance Modal Analysis

## Slide 15: Model description
Model of aggregated impedances (source and grid)
System is stable if satisfies Nyquist stability criterion
Key assumptions:
  Division point
  Source-grid or grid-source approach
Methods (III): Stability analysis model
Figure 12: Impedance model for stability analysis. [6]
Figure 13: Closed loop system for stability analysis. [6]

## Slide 16: Model description
Nyquist stability criterion in the Bode diagram
  Bode instead of Nyquist because of frequency information directly included
  Evaluation of stability for zero-dB crossings (intersection of source and grid impedances)
    At each intersection the phase angle is evaluated
    Due to the assumptions safety margin of 30⁰ introduced
Quality of stability evaluated by following phase margin at each resonant frequency:
Methods (IV): Stability assessment

## Slide 17: Model description
Topology cases
Figure 14: Network of considered offshore WPP.
Case 1
Case 2
Case 3

## Slide 18: Simulation results

## Slide 19: Simulations results
Impedance model
Case 1
Case 2
Case 3
Figure 16: Impedance model of Case 2.
Software: MATLAB
    Precision: 0.01 – 0.0001 order (0.5 – 0.005 Hz),
    Range: up to 30 order (1500Hz)
    150 kV equivalent circuit

## Slide 20: Simulations results
Nonlinear impedances of WT inverter and HVDC-link rectifier
Figure 17: WT inverter impedance
Figure 18: HVDC rectifier impedance

## Slide 21: Simulations results
Case 2: Frequency sweep
Figure 19: Frequency sweep curves of Case 2
Table 1: FS values of Case 2

## Slide 22: Simulations results
Case 2: Harmonic Resonance Modal Analysis – max. modes and all modes
Figure 20: HRMA - max. modes of Case 2
Figure 21: HRMA - modes of Case 2

## Slide 23: Simulations results
Case 2: Harmonic Resonance Modal Analysis – critical modes
Figure 22: HRMA – critical modes of Case 2
Table 2: HRMA key values of Case 2

## Slide 24: Simulations results
Chart: Case 2: VS model
8.46 | 5.3 | 7.9 | 8 | 8.7 | 9 | 9.2 | 12.5 | 8.7 | 9 | 9.2 | 12.5
12.12 | 0 | 0 | 0 | 0.2 | 0.3 | 1.1 | 48.4 | 0.2 | 0.3 | 1.1 | 48.4
12.23 | 0.3 | 0 | 0 | 0 | 0.1 | 0.8 | 48.9 | 0 | 0.1 | 0.8 | 48.9
23 | 0.6 | 8.9 | 9.6 | 13.6 | 14.2 | 11.7 | 1 | 13.6 | 14.2 | 11.7 | 1
Chart: Case 2: CS-WT model
7.77 | 1.7 | 3.2 | 3.2 | 4.2 | 4.6 | 5.8 | 31.3 | 4.2 | 4.6 | 5.8 | 31.3
9.51 | 0 | 0 | 0 | 0.1 | 0.3 | 1.1 | 48.5 | 0.1 | 0.3 | 1.1 | 48.5
10.25 | 1.5 | 1.1 | 1.1 | 0.4 | 0.2 | 0 | 47.4 | 0.4 | 0.2 | 0 | 47.4
22.98 | 0.6 | 8.9 | 9.6 | 13.7 | 14.3 | 11.8 | 0.7 | 13.7 | 14.3 | 11.8 | 0.7
Chart: Case 2: Z(s) model
9.51 | 1.8 | 3.5 | 3.6 | 4.6 | 5.1 | 6.1 | 29.7 | 4.6 | 5.1 | 6.1 | 29.7
12.34 | 0 | 0 | 0 | 0.2 | 0.3 | 1.1 | 48.4 | 0.2 | 0.3 | 1.1 | 48.4
23.11 | 0.7 | 8.8 | 9.5 | 13.6 | 14.2 | 11.7 | 1 | 13.6 | 14.2 | 11.7 | 1
Case 2: Harmonic Resonance Modal Analysis – participation factors
Table 3: PF values of Case 2
Figure 23: PF distribution of Case 2

## Slide 25: Simulations results
Case 2: Verification in Power Factory
Figure 24: Power Factory FS curves of VS and CS models – Case 2
Figure 25: Power Factory FS curves from multiple buses
Parallel resonance
Series resonance

## Slide 26: Simulations results
VS model: Comparison between topology cases by FS
VS model
CS-WT model
Z(s) model
Figure 26: Comparison of FS curves between topology cases – VS model
Table 4: Comparison of FS values

## Slide 27: Simulations results
VS model: Comparison between topology cases by HRMA
Figure 27: Comparison of HRMA curves between topology cases – VS model
Notes: Kolory

## Slide 28: Simulations results
Chart: 
8.59 | 8.8 | 12.8 | 13 | 14.2 | 14.6 | 15.1 | 21.5
12.17 | 0.1 | 0 | 0 | 0.2 | 0.4 | 1.8 | 97.4
23.7 | 0.9 | 14.6 | 15.7 | 23.1 | 24.3 | 20 | 1.4
Chart: 
8.46 | 5.3 | 7.9 | 8 | 8.7 | 9 | 9.2 | 12.5 | 8.7 | 9 | 9.2 | 12.5
12.12 | 0 | 0 | 0 | 0.2 | 0.3 | 1.1 | 48.4 | 0.2 | 0.3 | 1.1 | 48.4
12.23 | 0.3 | 0 | 0 | 0 | 0.1 | 0.8 | 48.9 | 0 | 0.1 | 0.8 | 48.9
23 | 0.6 | 8.9 | 9.6 | 13.6 | 14.2 | 11.7 | 1 | 13.6 | 14.2 | 11.7 | 1
Chart: 
7.55 | 2.5 | 4.8 | 4.9 | 5.1 | 5.2 | 5.2 | 5.2 | 5.1 | 5.2 | 5.2 | 5.2 | 4.9 | 5.1 | 5.2 | 5.2 | 5.2 | 5.1 | 5.2 | 5.2 | 5.2
12.1 | 0 | 0 | 0 | 0.1 | 0.2 | 0.6 | 24.2 | 0.1 | 0.2 | 0.6 | 24.2 | 0 | 0.1 | 0.2 | 0.6 | 24.2 | 0.1 | 0.2 | 0.6 | 24.2
12.12 | 0 | 0 | 0 | 0.2 | 0.3 | 1 | 46.6 | 0.2 | 0.3 | 1 | 46.6 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 1.8
12.3 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0.3 | 24.5 | 0 | 0 | 0.3 | 24.5 | 0.1 | 0 | 0 | 0.3 | 24.5 | 0 | 0 | 0.3 | 24.5
18.73 | 1.7 | 5.6 | 5.8 | 6.7 | 6.7 | 5.2 | 1.7 | 6.7 | 6.7 | 5.2 | 1.7 | 5.8 | 6.7 | 6.7 | 5.2 | 1.7 | 6.7 | 6.7 | 5.2 | 1.7
VS model: Comparison between topology cases: HRMA PF’s
Table 5: Comparison of FS values
Figure 28: PF distribution of VS model

## Slide 29: Simulations results
VS model: Comparison between topology cases: HRMA dominant buses
Table 6: Sources of resonances for VS model

## Slide 30: Simulations results
Case 2: Stability (I)
Figure 29: Bode diagram for stability analysis – Case 2

## Slide 31: Simulations results
Case 2: Stability (II)
Figure 30: Bode diagram (zoomed) for stability analysis – Case 2
Table 7: Phase margins for each resonant frequency – Case 2
  Safety margin:

## Slide 32: Simulations results
Z(s) model: FS vs. HRMA vs. Bode for all topology cases
Table 10: Bode diagram intersections for Z(s) model
Table 8: FS values for Z(s) model
Table 9: HRMA values for Z(s) model

## Slide 33: Summary
Output from the methods
Method/ Output | Series resonance frequency value | Parallel resonance frequency value | Information about source of resonance | Information about stability
Frequency Sweep | Yes | Yes | No | No
Harmonic Resonance Modal Analysis | No | Yes | Yes | Yes, limited
Bode diagram | No | Yes | No | Yes
Table 11: Comparison of methods’ output

## Slide 34: Summary
More resonant frequencies for cases with multiple branches
Downward shift of resonance for topology cases with more cables (more capacitance):
New resonant frequencies have expected values and expected source due to symmetry in the network
All three models are consistent with respect to sources of resonance
The resonance sourced near WT inverter is the ”stiffest”: minor shifting, highest PF’s and highest stability phase margin
Resonant frequencies of highest group (around 23th order) marked as unstable (unstable operation in case of presence of waveforms around this order)
Progressively worse stability phase margin for the topologies with more branches
Observations from simulations

## Slide 35: Summary
Recognition of resonant frequencies, their values and amount in a network
Identification of origins of resonances indicating the best locations for filters implementation
Prediction of new resonances and their approximate origins in case of topology change
Labeling each detected resonances with respect to hazard for stability
Mitigation of resonance by adjusting of converter impedance (detailed control data necessary)
Conclusions

## Slide 36: Thank you!
19 July 2016

## Slide 37: Reference (figures, equations)
[1] REN21, „Renewables 2016 - Global Status Report. Renewable Energy Policy Network for the 21st Century,” 2016.
[2] EWEA, „The European oshore wind industry - key trends and statistics 2015,” February 2016.
[3] N. Barberis Negra, J. Todorovic, T. Ackerman, „Loss evaluation of HVAC and HVDC transmission solutions for large offshore wind farms”.
[4] G. F. Reed, H. A. A. Hassan, M. J. Korytowski, P. T. Lewis, and B. M. Grainger, „Comparison of hvac and hvdc solutions for oshore wind farms with a procedure for system economic evaluation," in Energytech, 2013 IEEE
[5] H. Liu and J. Sun, „Voltage stability and control of oshore wind farms with ac collection and hvdc transmission," IEEE Journal of emerging and selected topics in power electronics, vol. 2, no. 4, pp. 1181-1189, 2014.
[6] J. Sun, „Impedance-based stability criterion for grid-connected inverters," IEEE Transactions on Power Electronics, vol. 26, no. 11, pp. 3075-3078, 2011.